## Def
Mapping between Dicam LAN and BACnet objects
The bridge currently only handles Present_Value property

Daikin A/C unit uses following object types for values we require:					Examples
Object Type	Abbrev	Enum	Value-Type		Conversion from LAN	Conversion to LAN	ASM airspace	Exponent	BACnet	LAN
Analog Input	AI	0	Real		Int16 => Real * Exp	Real / Exp => Int16	1	2	100.00F	10000F
Analog Output	AO	1	Real				2	2
Analog Value	AV	2	Real		Int16 => Real * Exp	Real / Exp => Int16	3	2	12.80F	1280F
Binary Input	BI	3	Enum 0/1		Int16 => Unsigned * Exp	Unsigned / Exp => Int16	4	2	1 (on)	100%
Binary Output	BO	4	Enum 0/1				5	2
Binary Value	BV	5	Enum 0/1		Int16 => Unsigned * Exp	Unsigned / Exp => Int16	6	2	0 (off)	0%
Multi State Input	MSI	13	Enum/UInt32				7	0
Multi State Output	MSO	14	Enum/UInt32				8	0
Multi State Value	MSV	19	Enum/UInt32		Int16 => Unsigned	Unsigned => Int16	9	0	7	7
Note: Exponents are fixed by object type (see bmObjMap[] table in client.c)

Mapping table:
Device (implicit)	Object Type	Instance	Exponent	R/W
Sensor1	AI (0)	1	2	R	Discharge Air Temp	-50.0-249.998F	F vs C?
Sensor2	AV (2)	39	2	R	Effective Discharge Air Setpt	-83.2..+147.2F
Sensor3	AV (2)	27	0	R	Alarm Value	Enumerated
Sensor4	AV (2)	24	0	R	Warning Alarm	Enumerated
Sensor5	AV (2)	25	0	R	Problem Alarm	Enumerated
Sensor6	AV (2)	13	2	R/W	Discharge Air Clg Setpoint	39.992-100.0F or 4.44-37.78C
Sensor7	AV (2)	17	2	R/W	Discharge Air Htg Setpoint	39.992-100.0F or 4.44-37.78C
Sensor8	AI (0)	0	2	R	Test server ADC0
Output1	MSV (19)	5	0	R/W	Application Mode	1=Off, 2=Heat, 3=Cool, 4=FanOnly, 5=Auto
Output2	MSV (19)	13	0	W	Clear Alarms	1=None, 5=ClrAllAlms
Output3	MSV (19)	15	0	R	Unit State	1=Off,...8=Clg
Output4	AV (2)	13	0	R/W	DAT Clg Setpoint	0-100F	(outchan level is forced to zero exponent)
Output5
Output6
Output7	BO (4)	0			Test server output 0
Output8	BO (4)	1			Test server output 1	Output logging uses OCACTUAL whereas remote setting uses OCLEVEL?

ASM mapping
Unit	LAN addr
Airspace	Object Type Encoding – see above
Message	Object Instance
Value	Converted value (16 bit)

Examples
TxAddr	RxAddr	LSM	LSV	D0	D1	D2	D3
CFC (10)	Bridge (29)	RET/Obj	ASASM	Instance				ASM request
Bridge	CFC	VAL/Obj	ASASM	Instance		LoValue	HiValue	Reply

CFC	Bridge	RET/0	ICRAW	Ch 0	DevAddr: Bridge/0			Sens0 request – translates to read Discharge Air Temp
Bridge	CFC	VAL/0	ICRAW	Ch 0	DevAddr: Bridge/0	LoReading	HiReading	Reply

CFC	Bridge	SET/0	OCLEVEL	Ch 0	Type: None/0	Level=1%		Set Output1 to 1% => Set Application Mode to Off (No reply)

Diagnostic LEDs
LED1 (Yellow) – lit when no rx from LAN
LED2 (Red) – lit when no rx from BACnet (cleared on successful Read Property ack)
Green LEDs are on 485 DE so only indicate that device is transmitting which will happen regardless of presence of activity on BACnet or LAN

## NEGene
Mapping table:
Device (implicit)	Object Type	Instance	Exponent	R/W	ICACTIVE					TRANE
Sensor1	AI (0)	1	2	R		Discharge Air Temp	-50.0-249.998F	F vs C?
Sensor2	AV (2)	39	2	R		Effective Discharge Air Setpt	-83.2..+147.2F
Sensor3	AV (2)	27	0	R		Alarm Value	Enumerated
Sensor4	AV (2)	24	0	R		Warning Alarm	Enumerated
Sensor5	AV (2)	25	0	R		Problem Alarm	Enumerated
Sensor6	AV (2)	13	2	R/W		Discharge Air Clg Setpoint	39.992-100.0F or 4.44-37.78C
Sensor7	AV (2)	17	2	R/W		Discharge Air Htg Setpoint	39.992-100.0F or 4.44-37.78C
Sensor8*	AI (0)	3	2	R/W	YES	Space Air Temp	0-100.00F	(was DSP AV/6)
Output1	MSV (19)	5	0	R/W		Application Mode	1=Off, 2=Heat, 3=Cool, 4=FanOnly, 5=Auto
Output2	MSV (19)	13	0	W		Clear Alarms	1=None, 5=ClrAllAlms
Output3	MSV (19)	15	0	R		Unit State	1=Off,...8=Clg
Output4	AV (2)	9	0	R/W		Occupied Clg Setpoint	0-100F	(outchan level is forced to zero exponent)
Output5	AV (2)	28	0	R/W		Space Temp Input	0-100F
Output6	AO (2)	2				Space Air Temp Set BAS	(Trane air temp set-point)
Output7	BO (4)	0				Test server output 0
Output8	BO (4)	1				Test server output 1

Additional ASMs
Instance
Analog Inputs (Airspace 1)
1	DATemp
3	SpaTemp
4	ExtTemp
8	FanCap
11	RH	Invalid
14	ConTemp	Same as DATemp
Analog Values (Airspace 3)
1	CoolCap
6	DSP
9	Occupied Cooling Setpoint
13	DAT Clg Set
15	OADPos
24	Warn
25	Prob
27	Alarm
28	Space Temp Input (give room temp to AHU)
39	DATSet
MSV (Airspace 9)
1	AHUSta
2	CoolSta
15	UnitSta

* Sensor8 is used by CFC to monitor bridge health and reset it if readings are lost – was originally intended to use DSP but this reading disappeared when switched to Occupied Cooling mode

## Trane
Mapping table:
Device (implicit)	Object Type	Instance	Exponent	R/W					TRANE
Sensor1	AI (0)	15	2	R	Space Air Temp	-50.0-249.998F	F vs C?
Sensor2	AI (0)	50	2	R	Space Air Setpoint Active	-83.2..+147.2F
Sensor3	BI (3)	165	0	R	Alarm relay status	Binary (0-1 => 0-100)
Sensor4	AV (2)	24	0	R	Warning Alarm	Enumerated	AI/7 – Supply fan speed
Sensor5	AV (2)	25	0	R	Problem Alarm	Enumerated	AI/52 – DATSet active
Sensor6	AV (2)	13	2	R/W	Discharge Air Clg Setpoint	39.992-100.0F or 4.44-37.78C	AI/9 – Exhaust damper
Sensor7	AV (2)	17	2	R/W	Discharge Air Htg Setpoint	39.992-100.0F or 4.44-37.78C	AI/10 – Return fan
Sensor8	BI (3)	15	0		Supply Fan Config	0-5.00 inches wc
Output1	MSV (19)	5	0	R/W	Application Mode	1=Off, 2=Heat, 3=Cool, 4=FanOnly, 5=Auto
Output2	MSV (19)	13	0	W	Clear Alarms	1=None, 5=ClrAllAlms
Output3	MSV (19)	15	0	R	Unit State	1=Off,...8=Clg
Output4	AV (2)	13	0	R/W	DAT Clg Setpoint	0-100F	(outchan level is forced to zero exponent)		AO/6	“When configured for VAV”
Output5	AV (2)	21	0	R/W	Fan capacity %				N/A	Use DSP setpoint but requires scaling??
Output6	AO (1)	2			Space Air Temp Set BAS	(Trane air temp set-point)	CFC setpoint transfer on 10/6
Output7	AO (1)	11			Space Sensor Temp	(Trane air temp sensor reading)	CFC air temp transfer on 10/7
Output8	BI (3)	15	0		Supply Fan Config	0 = cycling, 1 = continuous (on); for some reason this is written through BI 15 (not the more obvious BO 4), it appears the bridge does support writing through a BI
	BO (4)	8

Additional ASMs					TRANE
Instance
Analog Inputs (Airspace 1)
24	DATemp				AI/24
15	SpaTemp				AI/15
18	ExtTemp				AI/18
	FanCap				AI/8
	RH	Invalid			AI/16
	ConTemp	Same as DATemp
7	VFD (Supply) fan level				AI/7
52	DAT Set-point (minimum)				AI/52
87	Space Air Temp Local				AI/87

Analog Values (Airspace 3)
1	CoolCap				AI/1
6	DSP				AI/28 (or AI/29)
	DSP				AI/29
52	DAT Clg Set				AI/52
11	OADPos				AI/11
24	Warn				?
25	Prob				?
27	Alarm				?
52	DATSet				AI/52
MSV (Airspace 9)
	AHUSta				BI/3?
	CoolSta
	UnitSta				BI/3

AI	SpaTempSet				AI/74
	SpaTempSetLocal				AI/78
	SpaTempSetActive				AI/50

	SpaTempActive				AI/15

	SpaTempSetBAS				AO/2	Successful Write/Read of Present_Value but appears Out_Of_Service property needs to be set to “False” to enable this setpoint

## Feb16
Saved configs 2016-02-16
		NEGene (Daikin)		PFFGene (Trane)		NanceCoGene (Trane)		Old defaults	Trane diffs
Addr	Name	Byte		Byte		Byte
0	UNUSED	10		10		10		10	0
1	UNUSEDHI	0		0		0		0	0
2	MAC	10		10		10		10	0
3	BAUD	38		38		38		38	0
4	MAX_MASTER	20		20		20		20	0
5	DEVICE0	255		255		255		255	0
6	DEVICE1	255		255		255		255	0
7	DEVICE2	255		255		255		255	0
8	DEVICE3	255		255		255		255	0
9	APPID	11		11		11		11	0
10	APPIDHI	3		3		3		3	0
11	RESETS	125		66		243		35	177
12	RESETSHI	4		49		7		0	-42
13	LANADDR	10		10		10		10	0
14	LANTXCYCLE	3		3		3		3	0
15	TIMEOUT	15		15		15		15	0
16	ICACTIVE	128		15		255		0	240
17	SERVERMAC	18		18		18		18	0
18	L2B_OBJ0	0		0		0		0	0		Sensor1	AI (0)	15	2	R	Space Air Temp
19	L2B_INST0	1		15		15		1	0
20		2		0		0		2	0		Sensor2	AI (0)	50	2	R	Space Air Setpoint Active
21		39		50		50		39	0
22		2		3		3		2	0		Sensor3	BI (3)	165	0	R	Alarm relay status
23		27		165		165		27	0
24		2		2		0		2	-2		Sensor4	AV (2)	24	0	R	Warning Alarm
25		24		24		7		24	-17
26		2		2		0		2	-2		Sensor5	AV (2)	25	0	R	Problem Alarm
27		25		25		52		25	27
28		2		2		0		2	-2		Sensor6	AV (2)	13	2	R/W	Discharge Air Clg Setpoint
29		13		13		9		13	-4
30		2		2		0		2	-2		Sensor7	AV (2)	17	2	R/W	Discharge Air Htg Setpoint
31		17		17		10		17	-7
32		0		3		3		255	0		Sensor8	BI (3)	15	0		Supply Fan Config
33		3		15		15		255	0
34		19		19		19		19	0		Output1	MSV (19)	5	0	R/W	Application Mode
35		5		5		5		5	0
36		19		19		19		19	0		Output2	MSV (19)	13	0	W	Clear Alarms
37		13		13		13		13	0
38		19		19		19		19	0		Output3	MSV (19)	15	0	R	Unit State
39		15		15		15		15	0
40		2		2		2		2	0		Output4	AV (2)	13	0	R/W	DAT Clg Setpoint
41		9		13		13		13	0
42		2		255		255		255	0		Output5	AV (2)	21	0	R/W	Fan capacity %
43		28		255		255		255	0
44		255		1		1		255	0		Output6	AO (1)	2			Space Air Temp Set BAS
45		255		2		2		255	0
46		4		1		1		4	0		Output7	AO (1)	11			Space Sensor Temp
47		0		11		11		0	0
48		4		4		3		4	-1		Output8	BI (3)	15	0		Supply Fan Config
49	L2B_END	1		8		15		1	7
50	END	255		255		255		255	0
51		255		255		255		255	0
52		---		---		---		255
53		---		---		---		255
54		---		---		---		255
55		---		---		---		255
56		---		---		---		255
57		---		---		---		255
58		---		---		---		255
59		---		---		---		255
60		---		---		---		255
61		---		---		---		255
62		---		---		---		255
63		---		---		---		255
64		---		---		---		255
65		---		---		---		255
66		---		---		---		255
67		---		---		---		255
68		---		---		---		255
69		---		---		---		255
70		---		---		---		255
71		---		---		---		255
72		---		---		---		255
73		---		---		---		255
74		---		---		---		255
75		---		---		---		255
76		---		---		---		255
77		---		---		---		255
78		---		---		---		255
79		---		---		---		255
80		---		---		---		255
81		---		---		---		255
82		---		---		---		255
83		---		---		---		255
84		---		---		---		255
85		---		---		---		255
86		---		---		---		255
87		---		---		---		255
88		---		---		---		---
89		---		---		---		---
90		---		---		---		---
91		---		---		---		---
92		---		---		---		---
93		---		---		---		---
94		---		---		---		---
95		---		---		---		---
96		---		---		---		---
97		---		---		---		---
98		---		---		---		---
99		---		---		---		---
100		---		---		---		---
101		---		---		---		---
102		---		---		---		---
103		---		---		---		---
104		---		---		---		---
105		---		---		---		---
106		---		---		---		---
107		---		---		---		---
108		---		---		---		---
109		---		---		---		---
110		---		---		---		---
111		---		---		---		---
112		---		---		---		---
113		---		---		---		---
114		---		---		---		---
115		---		---		---		---
116		---		---		---		---
117		---		---		---		---
118		---		---		---		---
119		---		---		---		---
120		---		---		---		---
121		---		---		---		---
122		---		---		---		---
123		---		---		---		---
124		---		---		---		---
125		---		---		---		---
126		---		---		---		---
127		---		---		---		---
128		---		---		---		---
129		---		---		---		---
130		---		---		---		---
131		---		---		---		---
132		---		---		---		---
133		---		---		---		---
134		---		---		---		---
135		---		---		---		---
136		---		---		---		---
137		---		---		---		---
138		---		---		---		---
139		---		---		---		---
140		---		---		---		---
141		---		---		---		---
142		---		---		---		---
143		---		---		---		---
144		---		---		---		---
145		---		---		---		---
146		---		---		---		---
147		---		---		---		---
148		---		---		---		---
149		---		---		---		---
150		---		---		---		---
151		---		---		---		---
152		---		---		---		---
153		---		---		---		---
154		---		---		---		---
155		---		---		---		---
156		---		---		---		---
157		---		---		---		---
158		---		---		---		---
159		---		---		---		---
160		---		---		---		---
161		---		---		---		---
162		---		---		---		---
163		---		---		---		---
164		---		---		---		---
165		---		---		---		---
166		---		---		---		---
167		---		---		---		---
168		---		---		---		---
169		---		---		---		---
170		---		---		---		---
171		---		---		---		---
172		---		---		---		---
173		---		---		---		---
174		---		---		---		---
175		---		---		---		---
176		---		---		---		---
177		---		---		---		---
178		---		---		---		---
179		---		---		---		---
180		---		---		---		---
181		---		---		---		---
182		---		---		---		---
183		---		---		---		---
184		---		---		---		---
185		---		---		---		---
186		---		---		---		---
187		---		---		---		---
188		---		---		---		---
189		---		---		---		---
190		---		---		---		---
191		---		---		---		---
192		---		---		---		---
193		---		---		---		---
194		---		---		---		---
195		---		---		---		---
196		---		---		---		---
197		---		---		---		---
198		---		---		---		---
199		---		---		---		---
200		---		---		---		---
201		---		---		---		---
202		---		---		---		---
203		---		---		---		---
204		---		---		---		---
205		---		---		---		---
206		---		---		---		---
207		---		---		---		---
208		---		---		---		---
209		---		---		---		---
210		---		---		---		---
211		---		---		---		---
212		---		---		---		---
213		---		---		---		---
214		---		---		---		---
215		---		---		---		---
216		---		---		---		---
217		---		---		---		---
218		---		---		---		---
219		---		---		---		---
220		---		---		---		---
221		---		---		---		---
222		---		---		---		---
223		---		---		---		---
224		---		---		---		---
225		---		---		---		---
226		---		---		---		---
227		---		---		---		---
228		---		---		---		---
229		---		---		---		---
230		---		---		---		---
231		---		---		---		---
232		---		---		---		---
233		---		---		---		---
234		---		---		---		---
235		---		---		---		---
236		---		---		---		---
237		---		---		---		---
238		---		---		---		---
239		---		---		---		---
240		---		---		---		---
241		---		---		---		---
242		---		---		---		---
243		---		---		---		---
244		---		---		---		---
245		---		---		---		---
246		---		---		---		---
247		---		---		---		---
248		---		---		---		---
249		---		---		---		---
250		---		---		---		---
251		---		---		---		---
252		---		---		---		---
253		---		---		---		---
254		---		---		---		---
255		---		---		---		---
256		---		---		---		---
257		---		---		---		---
258		---		---		---		---
259		---		---		---		---
260		---		---		---		---
261		---		---		---		---
262		---		---		---		---
263		---		---		---		---
264		---		---		---		---
265		---		---		---		---
266		---		---		---		---
267		---		---		---		---
268		---		---		---		---
269		---		---		---		---
270		---		---		---		---
271		---		---		---		---
272		---		---		---		---
273		---		---		---		---
274		---		---		---		---
275		---		---		---		---
276		---		---		---		---
277		---		---		---		---
278		---		---		---		---
279		---		---		---		---
280		---		---		---		---
281		---		---		---		---
282		---		---		---		---
283		---		---		---		---
284		---		---		---		---
285		---		---		---		---
286		---		---		---		---
287		---		---		---		---
288		---		---		---		---
289		---		---		---		---
290		---		---		---		---
291		---		---		---		---
292		---		---		---		---
293		---		---		---		---
294		---		---		---		---
295		---		---		---		---
296		---		---		---		---
297		---		---		---		---
298		---		---		---		---
299		---		---		---		---
300		---		---		---		---
301		---		---		---		---
302		---		---		---		---
303		---		---		---		---
304		---		---		---		---
305		---		---		---		---
306		---		---		---		---
307		---		---		---		---
308		---		---		---		---
309		---		---		---		---
310		---		---		---		---
311		---		---		---		---
312		---		---		---		---
313		---		---		---		---
314		---		---		---		---
315		---		---		---		---
316		---		---		---		---
317		---		---		---		---
318		---		---		---		---
319		---		---		---		---
320		---		---		---		---
321		---		---		---		---
322		---		---		---		---
323		---		---		---		---
324		---		---		---		---
325		---		---		---		---
326		---		---		---		---
327		---		---		---		---
328		---		---		---		---
329		---		---		---		---
330		---		---		---		---
331		---		---		---		---
332		---		---		---		---
333		---		---		---		---
334		---		---		---		---
335		---		---		---		---
336		---		---		---		---
337		---		---		---		---
338		---		---		---		---
339		---		---		---		---
340		---		---		---		---
341		---		---		---		---
342		---		---		---		---
343		---		---		---		---
344		---		---		---		---
345		---		---		---		---
346		---		---		---		---
347		---		---		---		---
348		---		---		---		---
349		---		---		---		---
350		---		---		---		---
351		---		---		---		---
352		---		---		---		---
353		---		---		---		---
354		---		---		---		---
355		---		---		---		---
356		---		---		---		---
357		---		---		---		---
358		---		---		---		---
359		---		---		---		---
360		---		---		---		---
361		---		---		---		---
362		---		---		---		---
363		---		---		---		---
364		---		---		---		---
365		---		---		---		---
366		---		---		---		---
367		---		---		---		---
368		---		---		---		---
369		---		---		---		---
370		---		---		---		---
371		---		---		---		---
372		---		---		---		---
373		---		---		---		---
374		---		---		---		---
375		---		---		---		---
376		---		---		---		---
377		---		---		---		---
378		---		---		---		---
379		---		---		---		---
380		---		---		---		---
381		---		---		---		---
382		---		---		---		---
383		---		---		---		---
384		---		---		---		---
385		---		---		---		---
386		---		---		---		---
387		---		---		---		---
388		---		---		---		---
389		---		---		---		---
390		---		---		---		---
391		---		---		---		---
392		---		---		---		---
393		---		---		---		---
394		---		---		---		---
395		---		---		---		---
396		---		---		---		---
397		---		---		---		---
398		---		---		---		---
399		---		---		---		---
400		---		---		---		---
401		---		---		---		---
402		---		---		---		---
403		---		---		---		---
404		---		---		---		---
405		---		---		---		---
406		---		---		---		---
407		---		---		---		---
408		---		---		---		---
409		---		---		---		---
410		---		---		---		---
411		---		---		---		---
412		---		---		---		---
413		---		---		---		---
414		---		---		---		---
415		---		---		---		---
416		---		---		---		---
417		---		---		---		---
418		---		---		---		---
419		---		---		---		---
420		---		---		---		---
421		---		---		---		---
422		---		---		---		---
423		---		---		---		---
424		---		---		---		---
425		---		---		---		---
426		---		---		---		---
427		---		---		---		---
428		---		---		---		---
429		---		---		---		---
430		---		---		---		---
431		---		---		---		---
432		---		---		---		---
433		---		---		---		---
434		---		---		---		---
435		---		---		---		---
436		---		---		---		---
437		---		---		---		---
438		---		---		---		---
439		---		---		---		---
440		---		---		---		---
441		---		---		---		---
442		---		---		---		---
443		---		---		---		---
444		---		---		---		---
445		---		---		---		---
446		---		---		---		---
447		---		---		---		---
448		---		---		---		---
449		---		---		---		---
450		---		---		---		---
451		---		---		---		---
452		---		---		---		---
453		---		---		---		---
454		---		---		---		---
455		---		---		---		---
456		---		---		---		---
457		---		---		---		---
458		---		---		---		---
459		---		---		---		---
460		---		---		---		---
461		---		---		---		---
462		---		---		---		---
463		---		---		---		---
464		---		---		---		---
465		---		---		---		---
466		---		---		---		---
467		---		---		---		---
468		---		---		---		---
469		---		---		---		---
470		---		---		---		---
471		---		---		---		---
472		---		---		---		---
473		---		---		---		---
474		---		---		---		---
475		---		---		---		---
476		---		---		---		---
477		---		---		---		---
478		---		---		---		---
479		---		---		---		---
480		---		---		---		---
481		---		---		---		---
482		---		---		---		---
483		---		---		---		---
484		---		---		---		---
485		---		---		---		---
486		---		---		---		---
487		---		---		---		---
488		---		---		---		---
489		---		---		---		---
490		---		---		---		---
491		---		---		---		---
492		---		---		---		---
493		---		---		---		---
494		---		---		---		---
495		---		---		---		---
496		---		---		---		---
497		---		---		---		---
498		---		---		---		---
499		---		---		---		---
500		---		---		---		---
501		---		---		---		---
502		---		---		---		---
503		---		---		---		---
504		---		---		---		---
505		---		---		---		---
506		---		---		---		---
507		---		---		---		---
508		---		---		---		---
509		---		---		---		---
510		---		---		---		---
511		255		255		255		255